|  | # Aluflam North America 16604 Edwards Road Cerritos, CA 90703 Phone: 562.926.9520 Website: www.aluflam-usa.com |
| --- | --- |

# Aluflam Fire-Rated Aluminum 60 Min. Curtain Wall –

# 3-Part Specification

Notes to Specifier: This product specification is written to assist specifiers in the preparation of project specifications. The section must be carefully reviewed and edited to meet the requirements of the project and local building code. Section numbers are from MasterFormat 1995 Edition, with numbers from MasterFormat 2004 Edition in parentheses. Delete the version that is not required. Notes to the specifier are contained in boxes and should be deleted from final copy. Optional items requiring selection by the specifier are enclosed within brackets and highlighted in yellow. Make appropriate selections and delete others. When editing is complete, delete all text on this page, then remove the section break at the top of the next page to remove this page from the document. For assistance, call Aluflam North America at 562.926.9520.

# SPECIFICATION BEGINS ON THE FOLLOWING PAGE.

# SECTION 08910 (08 44 10)

FIRE-RATED ALUMINUM CURTAIN WALL

# PART 1 - GENERAL

  - SECTION INCLUDES

- Fire-rated aluminum curtain wall including frame and glazing which consist of the standard system CW-EI60 and the deeper frame system CW2-EI60.

  - RELATED SECTIONS

- Section 08817 (08 88 17): Fire-Rated Glass & Framing.

  - REFERENCES

A.	American Society for Testing and Materials (ASTM):

- ASTM E119 Standard Test Methods for Fire Tests of Building Construction and Materials.

- ASTM E2010 Standard Test Method for Positive Pressure Fire Tests of Window Assemblies.

- ASTM E 283-04, Test Method for Determining Rate of Airflow Through Exterior Windows, Curtain Walls and Doors Under Specified Pressure Differences Across the Specimen.

- ASTM E 330-02, Test Method for Structural Performance of Exterior Windows, Curtain Walls and Doors by Uniform Static Air Pressure Difference.

- ASTM E 331-00, Test Method for Water Penetration of Exterior Windows, Curtain Walls and Doors by Uniform Static Air Pressure Difference.

B.	National Fire Protection Association (NFPA):

- NFPA 80: Standard for Fire Doors and Fire Windows.

- NFPA 257: Standard on Fire Test for Window and Glass Block Assemblies.

C.	Uniform Building Code (UBC):

- UBC-7-4: Methods for Fire Tests of Window Assemblies.

D.	Underwriters Laboratories, Inc. (UL):

- UL 9: Fire Tests of Window Assemblies.

- UL 263: Fire Tests of Building Construction and Materials

E.	Standard Council of Canada:

- ULC Standard CAN4-S101: Fire Tests of Building Construction and Materials.

- ULC Standard CAN4-S106: Fire Tests of Door Assemblies.

F.	American National Standards Institute (ANSI):

- ANSI Z97.1 Safety Glazing Materials Used in Buildings – Safety Performance Specifications and Methods of Test.

G.	Consumer Product Safety Commission (CPSC):

- CPSC 16 CFR 1201 Categories I and II:  Safety Standard for Glazing Materials.

H.  American Architectural Manufacturers Association (AAMA)

- AAMA 501.1-05, Standard Test Method for Metal Curtain Walls for Water Penetration Using Dynamic Pressure.

  - SYSTEM DESCRIPTION

A.	Performance Requirements:

- Fire Rating: 60 minutes.

- Certification: Windows shall be tested in accordance with ASTM E 2010, NFPA 252, UBC 7-4, UL263, CAN4-S106.

- Testing Laboratory: Fire tests shall be conducted by an approved independent testing laboratory, similar to Underwriter’s Laboratories, Inc.

- Air Infiltration:  The test specimen shall be tested in accordance with ASTM E283 at a minimum frame size of 97" x 145". Air infiltration rate shall not exceed 0.00 cfm/ft of area at a static air pressure differential of 8 psf.

- Static Water Resistance: The test specimen shall be tested in accordance with ASTM E331 at a minimum frame size of 97" x 145".  There shall be no leakage as defined in test method at a static pressure differential of 8 psf.

- Dynamic Water Resistance: The test specimen shall be tested in accordance with AAMA 501.1 at a minimum frame size of 97" x 145".  There shall be no leakage as defined in test method at a dynamic pressure differential of 8 psf.

- Uniform Load Deflection: A minimum static air pressure difference of 100 psf shall be applied in the positive and negative direction in accordance with ASTM E330. There shall be no deflection in excess of L/175 of the span of any framing member. (This only cover the CW2-EI60 system)

- Uniform Load Structural Test: A minimum static air pressure difference of 150 psf shall be applied in the positive and negative direction in accordance with ASTM E330.

- Thermal Transmittance (U-value): When tested to AAMA Specification 503.1, the thermal transmittance (U-value) shall not be more than 0.48 BTU/hr/sf/˚F.

1.05 SUBMITTALS

A.	listed submittals in accordance with Conditions of the Contract and Division 1 Submittal Procedure Section.

- Shop Drawings: Submit shop drawings showing layouts, profiles and product components.

- Samples: Submit samples for finishes, colors and textures.

- Technical Information: Submit latest edition of manufacturer’s product data providing product description, technical data and installation instructions.

1.06 QUALITY ASSURANCE

A.	Listings and Labels:
Fire rated framing and glazing shall be under current follow-up services by an approved independent agency and maintain a current listing or certification. Assemblies shall be labeled in accordance with limits of listings.

1.07 DELIVERY, STORAGE AND HANDLING

A.	Ordering: Comply with manufacturer’s ordering instructions and lead-time requirements to avoid construction delays.

B.	Delivery: Deliver materials to specified destination in manufacturer’s packaging undamaged, complete with installation instructions.

C.	Storage and Protection: Store off ground, under cover, protected from weather, direct sunlight, construction activities and at temperature conditions recommended by manufacturer, +10°F to +110°F.

D.  Handling: Protect materials and finish during handling and installation to prevent damage.

1.08 PROJECT CONDITIONS

A.	Field Measurements: Verify actual measurements for openings by field measurements before fabrication. Show recorded measurements on shop drawings. Coordinate field measurements and fabrication schedule with construction progress to avoid construction delays.

# PART 2 - PRODUCTS

2.01 FIRE-RATED ALUMINUM FIXED WINDOWS

A.	Manufacturer: Aluflam North America

- Contact: 16604 Edwards Road, Cerritos, CA 90703: Telephone 562.926.9520 Fax 562.404.1394.  E-mail info@aluflam-usa.com Website  www.aluflam-usa.com, or local representative (www.aluflam-usa.com/contact/representatives.php).

2.02 MATERIALS – ALUMINUM FRAMING

  - Frame construction:  Integral structure, pressure plate, and cap from extruded aluminum profiles.  Filled internally with cement composite material.

  - Dimensions:

CW-EI60 
1.  Perimeter framing face dimension:  2 inch
2.  Depth of vertical framing:  5-3/16 inch
3.  Depth of horizontal framing:  5 inch

CW2-EI60

1.  Perimeter framing face dimension:  2 inch
2.  Depth of vertical framing:  7-5/8 inch
3.  Depth of horizontal framing:  7-13/16 inch

  - Assembly:  Frame corners assembled with mechanical fasteners – in factory or in the field.

  - Sealing:  Framing system shall insulate against effects of fire, smoke, and heat transfer from either side. Perimeter of the framing system to the rough opening shall be firmly packed with mineral wool insulation.

2.03 MATERIALS – FIRE RESISTANT GLAZING

- Assemblies shall be glazed with 60 minute rated 1 inch thick SGG Contraflam 60 fire resistant glazing material as manufactured by Vetrotech Saint-Gobain (www.vetrotechusa.com).

    - Individual lites shall be permanently identified with a listing mark.

    - Glazing material installed in “Hazardous Locations” (subject to human impact) shall be certified to meet the applicable requirements for fire rated assemblies referenced in ANSI Z97.1 Standard for Safety Glazing Materials Used In Buildings and/or CPSC 16 CFR 1201 Safety Standard for Architectural Glazing Materials.

    - Visible daylight transmission shall be a minimum of 81%. Glazing material shall be optically clear, colorless and free from unusual distortion.

Notes to Specifier: Specify the following paragraph for exterior applications.

- Fire-rated glazing shall be insulated with ¼” airgap and ¼” low-E coated outboard glass lite.  Installation conditions shall be analyzed to assure that fire-rated glazing is not exposed to temperatures outside the 10 – 110 degrees F limits.

2.04 MATERIALS – GLAZING AND ASSEMBLY ACCESSORIES

  - Fasteners: All fasteners, setting pads, and glazing clips, shall be stainless or zinc-plated steel.

B.	Glazing Accessories: The glazing material perimeter shall be separated from the perimeter framing system with approved flame retardant intumescent glazing tape.  Ceramic setting blocks shall be placed between the metal setting pads and the glazing material. Setting pads and blocks provided by manufacturer.

2.05 FABRICATION

- Curtainwall frames shall be furnished pre-assembled or K-D. Curtainwall assemblies shall be field glazed.

- Fabrication Dimensions:  Fabricate to approved dimensions.  The general contractor shall guarantee dimensions within required tolerance (+ - 1/8”).  Obtain approved shop drawings prior to fabrication.

2.06 FINISHES

A.	Framing shall be chemically cleaned and pretreated, then finished on all exposed areas with:

Notes to Specifier: Select finish and color.

[Anodized – Clear] [Anodized – Light Bronze] [Anodized – Medium Bronze] [Anodized – Dark Bronze] [Powder Coated Epoxy – Color RAL#XXXX] [Fluoropolymer – (Kynar – Duranar) Specify UC Code/Color].

B.	Protect finishes on exposed surfaces from damage by applying a strippable, temporary protective covering before shipping.

C.  Slight variations in appearance of abutting or adjacent pieces are acceptable.  Noticeable variations in the same piece are not acceptable.

# PART 3 - EXECUTION

3.01 EXAMINATION

A.	Examine area to receive curtainwall.  Openings shall be plumb, square and within allowable tolerances.  Notify Architect of conditions that would adversely affect installation or subsequent use.  Do not proceed with installation until unsatisfactory conditions are corrected.

3.02 INSTALLATION

A.	Curtainwall installation shall be by a specialty contractor with appropriate experience qualifications; and in strict accordance with the approved shop drawings.

3.03 CLEANING

A.	Cleaning: Remove temporary coverings and protection of adjacent work areas. Glass and frame should be cleaned using soft clean cloth, chamois leathers, sponges or soft paper.  Use clean warm water with a mild detergent. Do not use detergent that contains either alkaline, acids or fluoride! Abrasive cleaning methods can damage surfaces!  Clean prior to owner’s acceptance. Remove construction debris from project site and legally dispose of debris.

## END OF SECTION